## Slide 1: Closed Area Construction
MFC Physical Security
Robert Pullen
Industrial Security Representative Stf

## Slide 2: What Are the Requirements?
Basic Closed Area requirements are outlined in NISPOM
  Chapter 5, Section 8
Closed areas are constructed to protect classified assets that can not be stored in approved GSA safes primarily due to their size
Questions you should ask yourself when constructing a closed area
  What is the area going to be used for?
    Protection of hardware
    Discussions
    Classified computer processing

## Slide 3: What Are the Requirements?
Different requirements may drive additional considerations when building the area
    Sound considerations
    Visual access
    Size of material
    Movement of equipment in/out of area

## Slide 4: Walls
Wall construction material must offer resistance and be capable of showing evidence of unauthorized entry or removal
  Concrete block
  Gypsum board
  Insert type panels
  Other non-conventional items like opaque glass
Perimeter walls must to extend to the true ceiling of the area
Walls can be constructed of non-opaque material if visual access is not a factor

## Slide 5: Ceilings
True ceiling shall be constructed of similar type materials as walls
Wire mesh or other non-opaque material that offers similar resistance and evidence of unauthorized entry may be used when visual access to classified is not a factor
The use of ceiling tile clips to re-enforce a false ceiling may no longer be used in lieu of extending walls to the true ceiling deck

## Slide 6: Windows
Can my closed area have windows?
  Yes, however additional considerations must be taken
    Windows that can be opened or are less than 18 feet from an access point must be protected
      18 Gauge expanded metal
      ½ inch bars no more than 6 inches apart with cross bars to prevent spreading
    Visual factors must also be taken into consideration
      Drapes, blinds or other practical methods to prevent visual access must be employed

## Slide 7: Windows
  Windows must remain closed during non working hours and securely fastened to preclude surreptitious entry at all times
  Windows that cannot be opened should also be afforded a level of protection
    Motion protection
    Glass breaks
  Windows that are greater than 18 feet from an access point require no additional physical protection
    Visual factors should still be considered

## Slide 8: Miscellaneous openings
Miscellaneous openings over 96 square inches, or greater and over 6 inches at their smallest dimension require the installation of one of the following
  ½ inch diameter steel bars with maximum space between bars no greater than 6 inches
  Grills consisting of 18 gauge expanded metal, wire mesh or equivalent gauge commercial metal duct barrier
Barriers must be installed in a manner that prevents removal from outside the area
  Welded or pop riveted to the duct

## Slide 9: Miscellaneous openings
Inspection ports in HVAC ducts should be installed to allow inspection of security screens
Inspection ports should be on the portion of the duct inside the closed area
An approved IDS system (motion detection) may be used in lieu of a barrier

## Slide 10: Doors
Doors should be either solid core wood or metal clad doors to offer the greatest resistance and detection of unauthorized entry
  If doors have windows, louvers or other accessible openings they must be secured with 18 gauge expanded metal or wire mesh
  Where visual access is a factor windows shall also be covered

## Slide 11: Doors
When double doors are used an astragal (overlapping molding) is required
  Astragals should be attached to the door in a manner that prevents removal
  Screw heads if exposed to attach an astragal should have the heads knurled out to prevent removal
Astragal

## Slide 12: Hardware
Make sure heavy gauge hardware is used (Construction Grade)
  Hasp & Staple
  Hinges
  Slide bolts
Welded hinge
Security pinned hinge

## Slide 13: Hardware
    Ensure all hardware is installed to preclude removal
      Mounting hardware should only be accessible from inside the protected space
      Where hardware is accessible from the exterior, tamper proof hardware must be used or modified
Bolts peened to prevent removal

## Slide 14: Locking devices
Primary entry door are required to be equipped with one of the following
  Approved built in combination lock
    Kaba-Mas CDX-09
    S&G 2740
  Approved combination padlock
    S&G 8088
  Approved key operated padlock
    Key protection requirements, NISPOM 5-310

## Slide 15: Locking devices
Additional doors shall be securable from inside the area using panic bars, slide bolts or locking bars

## Slide 16: Access control
During hours when the closed area is occupied unauthorized access to the area must be controlled
  Methods that can be used
    Personnel controls
    Access control device
      Simplex lock
    Access control system
      Requires both badge & pin
Access control devices are not approved by themselves for securing an area when not occupied

## Slide 17: Intrusion Detection System (IDS)
An IDS is required for all closed areas protecting Secret or Top Secret material
  Closed area protecting material only classified to the Confidential level do not require an IDS but must meet all of the previous addressed construction requirements
The IDS must be monitored by a central monitoring station
  Government Contractor Monitoring Station (GCMS)
  Cleared commercial central station
  Cleared protective signal service station
  Cleared residential monitoring station

## Slide 18: Intrusion Detection System (IDS)
Approved IDS systems must meet Underwriter Laboratories (U.L.) 2050 standards
Alarm service company installing the system must be a U.L. certified installer
Installation of the IDS must meet “Extent 3” which requires all accessible openings to be monitored

## Slide 19: Questions?